December 2018

| Americas Bosch Security Systems, Inc. 130 Perinton Parkway Fairport, New York, 14450, USA Phone: + 1 800 289 0096 Fax: +1 585 223 9180 security.sales@us.bosch.com www.boschsecurity.us | Europe, Middle East, Africa Bosch Security Systems B.V. P.O. Box 80002 5617 BA Eindhoven, The Netherlands Phone: + 31 40 2577 284 Fax: +31 40 2577 330 emea.securitysystems@bosch.com www.boschsecurity.com | Asia-Pacific Robert Bosch (SEA) Pte Ltd, Security Systems 11 Bishan Street 21 Singapore 573943 Phone: +65 6571 2808 Fax: +65 6571 2699 apr.securitysystems@bosch.com www.boschsecurity.asia |
| --- | --- | --- |

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, based on MasterFormat 2004 and The Project Resource Manual—CSI Manual of Practice. The Manufacturer is responsible for technical accuracy.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Words and sentences within brackets [ ] are choices to include or exclude a particular item or statement.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.

SECTION 28 23 29

VIDEO SURVEILLANCE REMOTE DEVICES AND SENSORS

Bosch FLEXIDOME IP panoramic 6000 outdoor camera

Bosch FLEXIDOME IP panoramic 7000 outdoor camera

- – GENERAL

  - SUMMARY

    - Section Includes

      - Video Surveillance Remote Devices.

    - Related Sections

      - Section [28 23 13 – Video Surveillance Control and Management Systems].

      - Section [28 23 16 – Video Surveillance Monitoring and Supervisory Interfaces].

      - Section [28 23 19 – Digital Video Recorders and Analog Recording Devices].

      - Section [28 23 23 – Video Surveillance Systems Infrastructure].

**********Specifier’s note: Include those standards referenced elsewhere in this SECTION.

  - REFERENCES

    - Australia and New Zealand Standards

      - AS/NZS CISPR 32 Information technology equipment - Radio disturbance characteristics - Limits and methods of measurement

      - Conforms to RCM standards

    - Canadian Standards Association (CSA)

      - CAN/CSA-C22.2 No. 60950-1 Information Technology Equipment - Safety - Part 1: General Requirements (Bi-National standard, with UL 60950-1)

      - CAN/CSA-C22.2 No. 60950-22-07 Edition1 Information Technology Equipment - Safety - Part 22: Equipment to be Installed Outdoors (Bi-National standard, with UL 60950-22)

      - Conforms to cUL standards

    - European Norm

      - EN 50121-4:2016 Railway Applications - Electromagnetic Compatibility - Part 4: Emission And Immunity Of The Signaling And Telecommunications Apparatus

      - EMC directive 2014/30/EU

      - EN 50130-4:2001+A1:2014 (CE) Alarm Systems, Part 4 – Electromagnetic Compatibility – Product Family Standard: Immunity Requirements for Components of Fire, Intruder and Social Alarm Systems.

      - EN 50130-5: Alarm Systems, Part 5 – Environmental Test Methods (corresponds with VDE 0830 parts 1-5)

      - EN 50132-5-2: Alarm systems - CCTV surveillance systems for use in security applications - Part 5-2: IP Video Transmission Protocols

      - EN 55032, Class B – Information Technology Equipment – Radio Disturbance Characteristics – Limits and Methods of Measurement for Emission

      - EN 55024 Information technology equipment. Immunity characteristics. Limits and methods of measurement

      - EN60950-1: 2006+A11:2009+A1:2010+A12:2011+A2:2013 – Safety of information technology equipment (IT Equipment)

      - EN 60950-22: 2006/A11:2008

      - CE Declaration of Conformity

      - CB scheme

    - Federal Communications Commission (FCC) (www.fcc.gov)

      - FCC CFR 47 part 15; subpart B, Class B Digital Devices

    - Industry Canada

      - ICES-003 Class B Spectrum Management and Telecommunications Policy Interference-Causing Equipment Standard

    - International Electrotechnical Commission (IEC):

      - IEC 62676-2-3: Video surveillance systems for use in security applications – Part 2-3: Video transmission protocols – IP interoperability implementation based on WEB services.

      - IEC 62471 (IR version): Photobiological safety of lamps and lamp systems.

    - International Organization for Standardization (ISO)

      - 9001: Quality System

    - Underwriters Laboratories, Inc. (UL) (www.ul.com)

      - UL 60950-1 UL Standard for Safety of Information Technology Equipment.

      - UL 60950-22 Information Technology Equipment – Safety - Part 22: Equipment to be installed outdoors

    - Voluntary Control Council for Interference (VCCI)

      - VCCI-CISPR 32:2016

    - EurAsion Standards

      - EurAsian Conformity (EAC, Russian: Евразийское соответствие) - The products conforms to all technical regulations of the Eurasian Customs Union assessment procedures. It can be serviced in the territory of all Customs Union member countries: Russia, Belarus, Armenia, Kazakhstan and Kyrgyzstan

  - DEFINITIONS

    - Sensitivity: refers to the minimum level of light the sensor needs to generate an acceptable video picture, and is measured in lux.

    - Day/Night (infrared sensitive): The camera has normal color operation in situations where there is sufficient illumination (day conditions), but when there is little light available (night conditions) the sensitivity is increased.

    - IDNR (Intelligent Dynamic Noise Reduction): The intelligent Dynamic Noise Reduction applies temporal noise filtering when no motion is detected. The filtering reduces the noise in the image and this makes the encoder step more effective.

  - SYSTEM DESCRIPTION

    - Video Surveillance Remote Devices

      - NDS-6004-F180E FLEXIDOME IP panoramic 6000 outdoor camera

      - NDS-6004-F360E FLEXIDOME IP panoramic 6000 outdoor camera

      - NDS-7004-F180E FLEXIDOME IP panoramic 7000 outdoor camera

      - NDS-7004-F360E FLEXIDOME IP panoramic 7000 outdoor camera

    - Performance Requirements

      - Complete outdoor network video surveillance system inside a dome camera

      - 1/2.3-inch CMOS HD with progressive scan.

      - 180° or 360° panoramic coverage.

      - 12MP / 30 fps sensor for fine details with smooth motion.

      - Edge or client-side dewarping for easy integration.

      - Full resolution circular image recording.

      - Intelligent Dynamic Noise Reduction (iDNR) technology.

      - Intelligent streaming technology for reduced bitrates

      - DORI (Detect, Observe, Recognize, Identify) coverage.

      - Built-in Essential Video Analytics or Intelligent Video Analytics to trigger relevant alerts and quickly retrieve data.

      - Local storage with SD card.

      - Intelligent dynamic noise reduction to reduce bitrate by up to 50%.

      - ONVIF conformant.

  - SUBMITTALS

    - Submit under provisions of Section [01 33 00].

    - Product Data:

      - Manufacturer’s data, user and installation manuals for all equipment and software programs including computer equipment and other equipment required for complete video management system.

    - Shop Drawings; include

      - System device locations on architectural floor plans.

      - Full Schematic of system, including wiring information for all devices.

    - Closeout Submittals

      - User manual.

      - Parts list.

      - System device locations on architectural floor plans.

      - Wiring and connection diagram.

      - Maintenance requirements.

  - QUALITY ASSURANCE

    - Manufacturer:

      - Minimum of [20] years experience in manufacture and design Video Surveillance Devices.

      - Manufacturer’s quality system: Registered to ISO 9001:2005 Quality Standard.

    - Video Surveillance System

      - Listed by [UL] [EN] [FCC] specifically for the required loads.  Provide evidence of compliance upon request.

    - Installer:

      - Minimum of [5] years experience installing Video Surveillance Systems.

  - DELIVERY, STORAGE AND HANDLING

    - Comply with requirements of Section [01 60 00].

    - Deliver materials in manufacture’s original, unopened, undamaged containers; and unharmed original identification labels.

    - Protect store materials from environmental and temperature conditions following manufacturer’s instructions.

    - Handle and operate products and systems according to manufacturer’s instructions.

    - Bosch provides off-the-shelf availability for our top selling products and same-day or 24-hour shipping.

  - WARRANTY

    - Provide manufacturer’s warranty covering [3] years for replacement and repair of defective equipment.

  - MAINTENANCE

    - Make ordering of new equipment for expansions, replacements, and spare parts available to dealers and end users.

    - Provide factory direct technical support from 8:00 a.m. to 8:00 p.m. via phone and e-mail.

- – PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer:

[Bosch Security Systems, Inc.

130 Perinton Parkway

Fairport, New York, 1450, USA

Phone: + 1 800 289 0096

Fax: + 1 585 223 9180

security.sales@us.bosch.com

www.boschsecurity.us]

[Bosch Security Systems B.V.

P.O. Box 80002

5617 BA Eindhoven, The Netherlands

Phone: + 31 40 2577 284

Fax: +31 40 2577 330

emea.securitysystems@bosch.com

www.boschsecurity.com]

[Robert Bosch (SEA) Pte Ltd, Security Systems

11 Bishan Street 21

Singapore 573943

Phone: +65 6571 2808

Fax: +65 6571 2699

apr.securitysystems@bosch.com

www.boschsecurity.com]

    - Substitutions: [Not permitted.] [Under provisions of Division 1.]

      - [All proposed substitutions must be approved by the Architect or Engineer professional.]

      - [Proposed substitutions must provide a line-by-line compliance documentation.]

**********Specifier’s note: Select Camera System Series based on project requirement.

  - FLEXIDOME IP panoramic 6000 / 7000 camera
[NDS-6004-F180E], [NDS-6004-F360E], [NDS-7004-F180E], [NDS-7004-F360E]

    - General Characteristics:

      - The camera shall offer full 180° or 360° panoramic surveillance with complete area coverage, fine details and high speeds (12MP @ 30 fps sensor).

      - The camera shall offer full situational awareness and simultaneous E-PTZ views.

      - The camera shall provide edge or client-side dewarping for easy integration.

      - The camera shall be capable of operating in an indoor and an outdoor environment.

      - The camera shall use the DORI (Detect, Observe, Recognize, Identify) standard system (EN-50123-7) to distinguish persons or objects within a covered area.

      - The camera shall utilize Intelligent Dynamic Noise Reduction (iDNR) technology to reduce the bitrate and storage requirements by removing noise artifacts

      - The camera shall offer Intelligent streaming possibilities.

      - The camera shall offer tamper detection and Intelligent Video Analytics or Essential Video Analytics.

      - The camera shall provide direct network connection using H.264 and JPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

      - The camera shall work with Power over Ethernet IEEE 802.3af (802.3at type 1) for indoor applications with a compliant power supply source.

      - The camera shall support AutoMDIX.

      - A user shall be able to view video on a PC using a Web browser, with the Bosch Video Management System, Bosch Video Client or Bosch Video Security Client.

      - The cameras shall provide Intelligent Auto Exposure (IAE) to improve visibility of high contrast scenes (dark objects against a light background and the reverse).

      - The camera shall provide configurable scene modes that give optimized settings for distinct applications.

      - The camera shall provide multiple independent, fully programmable privacy mask areas.

      - The camera shall utilize pixel-by-pixel analysis to automatically compensate for bright areas of a high contrast scene without having to define a window or area.

    - Image processing and compression

      - The camera shall use a 1/2.3-inch CMOS image sensor.

      - The camera shall offer a video resolution of 12MP @30fps sensor

      - The camera shall use 2640 x 2640 sensor pixels [NDS-6004-F360E], [NDS-7004-F360E] or 3648 x 2160 sensor pixels [NDS-6004-F180E], [NDS-7004-F180E]

      - The camera shall be fitted with a 1.6 mm, F2.8 lens with a view angle of 360° [NDS-6004-F360E], [NDS-7004-F360E] or a 2.1 mm, F2.8 lens with a view angle of 180° [NDS-6004-F180E], [NDS-7004-F180E]

      - The camera shall have a dynamic range of 92 + 16 dB

      - The camera shall offer a minimum sensitivity of 0.55 lx in color and 0.18 lx in mono [NDS-6004-F360E], [NDS-7004-F360E] or 0.46 lx in color and 0.15 lx in mono [NDS-6004-F180E], [NDS-7004-F180E]

      - The camera automatic electronic shutter shall offer a shutter speed of 1/12 to 1/15000.

      - The camera shall be capable of capturing and storing images using the following compression standards:

        - H.264 MP (Main Profile)

        - M-JPEG

    - Network Video

      - The camera shall provide direct network connection using H.264 and M-JPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

      - The camera shall allow full camera control and configuration capabilities over the network.

      - The camera shall deliver video, at rates up to 30 images per second, via TCP/IP over a 10/100 Base-T, auto-sensing, half/full duplex, RJ45 Ethernet connection.

      - The camera shall support AutoMDIX.

      - The camera shall conform to the ONVIF Profile S, ONVIF Profile G, ONVIF Profile T standard and GB/T 28181.

      - The camera shall conform to protocols: IPv4, IPv6, UDP, TCP, HTTP, HTTPS, RTP/RTCP, IGMP V2/V3, ICMP, ICMPv6, RTSP, FTP,  ARP, DHCP, APIPA (Auto-IP, link local address), NTP (SNTP), SNMP (V1, V3, MIB-II), 802.1x, DNS, DNSv6, DDNS (DynDNS.org, selfHOST.de, no-ip.com), SMTP, iSCSI, UPnP (SSDP), DiffServ (QoS), LLDP, SOAP, Dropbox™, CHAP, Digest Authentication.

    - Image Posting

- The camera shall offer periodic JPEG image posting to an FTP server or a Dropbox account.

- The camera shall offer best face detection and JPEG best face image posting to an FTP server or to a Dropbox account.

    - Access Security

      - The camera shall offer three levels of password protection.

      - The camera shall support 802.1x authentication using a RADIUS (Remote Authentication Dial In User Service) server.

      - The camera shall store an SSL certificate for use with HTTPS.

      - The camera shall be capable of being independently AES encrypted with 128-bit keys.

    - Recording and Storage Management

      - The camera shall support iSCSI devices to allow video stream to be recorded directly to an iSCSI RAID array.

      - The camera shall support iSCSI storage targets to enable the camera to function as a conventional DVR.

      - The camera shall have an SD card slot for local storage (up to 2 TB) that supports security rated SD cards with health monitoring

      - The local storage feature shall be capable of storage for Automatic Network Replenishment (ANR).

      - Local Recording: Continuous recording, ring recording, alarm/events/schedule recording.

    - Alarm Handling Features:

      - The camera shall provide the capability on alarm to display up to a 31 character, programmable alarm message.

      - The camera shall provide email alarm messaging with optional JPEG posting.

    - Embedded Video Content Analysis

      - The camera shall be VCA enabled.

      - The camera shall be capable of processing and analyzing video within the camera itself, with no extra hardware required.

      - The camera shall be capable of detecting and sending alarms for abnormal events.

      - The camera shall allow users to set up to 10 separate profiles and switch profiles based on a day/night or holiday schedules.

      - The camera [NDS-7004-F180E], [NDS-7004-F360E] shall offer Intelligent Video Analysis (IVA) that uses an Intelligent tracker to follow objects within the defined regions of interest.

      - The camera [NDS-6004-F180E], [NDS-6004-F360E] shall offer Essential Video Analytics that uses an Intelligent tracker to follow objects within the defined regions of interest.

      - The camera shall offer MOTION+ video motion analysis that uses an algorithm based on pixel change and includes object size filtering and tamper-detection capabilities.

    - Electrical

      - The camera shall accept Power over Ethernet (48 VDC nominal).

      - The camera shall conform to the IEEE 802.3af (802.3at Type 1) compliant Power over Ethernet network. Power level: Class 1.

      - The camera shall consume typically 140 mA [NDS-6004-F180E], [NDS-6004-F360E] or 200 mA [NDS-7004-F180E], [NDS-7004-F360E]

    - Surveillance Software

      - The camera shall be accessible from a web browser, with the Bosch Video Management System, with the free-of-charge Bosch Video Client or Video Security Client, or via third-party software.

      - The camera shall be accessible from the Bosch Security System mobile app.

    - Environmental

      - The camera shall operate in a -30°C to +45°C (-22°F to 113°F) temperature range.

      - The camera shall offer IP66 ingress protection and a NEMA 4X enclosure

      - The camera shall offer IK10 impact protection.

    - Mechanical

      - The camera dimensions shall be:

        - Diameter 174.9 mm (6.88 in.)

        - Height 86.1 mm (3.39 in.).

      - The camera weight shall be 2060 g (4.54 lb) approx.

      - The camera color is RAL 9003.

  - ACCESSORIES

    - Mounting

      - NDA-U-PMT Pendant ceiling mount

      - NDA-U-PMTE Pendant ceiling extension pipe

      - NDA-U-PSMB Pendant ceiling mount SMB

      - NDA-8000-PIP Pendant interface plate excluding weather protector

      - NDA-8000-PIPW Pendant interface plate including weather protector

    - Other

      - NPD-5001-POE Power-over-Ethernet midspan injector for use with PoE enabled cameras; 15.4 W, 1-port

      - NPD-5004-POE Power-over-Ethernet midspan injectors for use with PoE enabled cameras; 15.4 W, 4-ports

      - NPD-3001-WAP Bosch camera portable and wireless installation tool

- – EXECUTION

  - EXAMINATION

    - Examine areas to receive devices and notify adverse conditions affecting installation or subsequent operation.

    - Do not begin installation until unacceptable conditions are corrected.

  - PREPARATION

    - Protect devices from damage during construction.

  - INSTALLATION

    - Install devices in accordance with manufacturer’s instruction at locations indicated on the floor drawings plans.

    - Ensure selected location is secure and offers protection from accidental damage.

    - Location must provide reasonable temperature and humidity conditions, free from sources of electrical and electromagnetic interference.

  - FIELD QUALITY CONTROL

    - Test snugness of mounting screws of all installed equipment.

    - Test proper operation of all video system devices.

    - Determine and report all problems to the manufacturer’s customer service department.

  - ADJUSTING

    - Make proper adjustment to video system devices for correct operation in accordance with manufacturer’s instructions.

    - Make any adjustment of camera settings to comply with specific customer’s need.

  - DEMONSTRATION

    - Demonstrate at final inspection that video management system and devices function properly.

END OF SECTION