IQSIGHT is a leading global supplier of security, safety, and communications products and systems. Protecting lives, buildings, and assets is the major aim. The product portfolio includes video security, intrusion detection, and fire detection as well as access control and management systems.

For additional information, contact:

| Americas IQSIGHT LLC 130 Perinton Parkway Fairport, New York, 14450 USA Phone: +1-800-289-0096 Fax: +1-800-315-0470 video.systems@iqsight.com https://www.iqsight.com | Europe, Middle East, Africa IQSIGHT B.V. Achtseweg Zuid 173 5651 GW Eindhoven The Netherlands Phone: + 31 40 2577 202 Fax: +31 40 2577 330 video.systems@iqsight.com https://www.keenfinity-group.com | Asia-Pacific KEENFINITY PTE. LTD. 11 Bishan Street 21 Singapore 573943 Phone: +65 6571 2600 Fax: +65 6571 2698 video.systems@iqsight.com apr.sales@keenfinity-group.com https://www.keenfinity-group.com |
| --- | --- | --- |

VIDEO SURVEILLANCE REMOTE DEVICES AND SENSORS

Multi dome 4x3MP 3.2-8.1mm IP66 IR

DIVISION 28 – ELECTRONIC SAFETY AND SECURITY

28 20 00 	Video Surveillance

28 21 00 	Surveillance Cameras

28 21 13	IP Cameras

Notes to Specifier:

1.  Where several alternative parameters or specifications exist, or where, the specifier has the option of inserting text, such choices are presented in <bold bracketed text>.

2.  Explanatory notes and comments are presented in italicized colored text.

Multi dome 4x3MP 3.2-8.1mm IP66

- GENERAL

  - SUMMARY

    - Section includes a 4x3 MP multi-imager camera with four independent imagers and motorized zoom/focus lenses that allow for full 360º coverage, integrated surround IR illumination, H.264 and H.265 encoding, dynamic range of 120 dB, and built-in artificial intelligence providing full situational awareness and triggers for relevant alerts.

## Related Requirements

      - 28 05 00 Common Work Results

      - 28 05 07.13 Power Sources for Video Surveillance

      - 28 05 07.21 PoE Power Sources for Electronic Safety and Security

      - 28 05 11 Cyber Security Requirements for Electronic Safety and Security

      - 28 05 19.13 Hybrid Digital Video Recorders

      - 28 05 19.15 Network Video Recorders

      - 28 05 33 Safety and Security Network Communications Equipment

      - 28 06 20 Schedules for Video Surveillance

      - 28 21 19 Camera Mounts

      - 28 23 00 Video Management System

      - 27 15 00 Communications Horizontal Cabling

      - 27 20 00 Data Communications

      - 28 16 15 Access Control Interfaces to Video Surveillance

      - 28 31 31.15 Intrusion Detection Interfaces to Video Surveillance

      - 28 51 15.13 Information Interfaces to Video Surveillance Systems

    - Sustainability

      - The fixed network camera shall be manufactured in compliance with ISO 9001 and ISO 14001.

      - The fixed network camera shall be compliant with the EU Directives 2011/65/EU (RoHS) and 2012/19/EU (WEEE).

      - Packaging shall be compliant with EU Directive 94/62/EC (amended by 2004/12/EC).

      - The fixed network camera shall be compliant with the EU regulation 1907/2006 (REACH).

  - REFERENCES

    - Abbreviations

      - AI – Artificial Intelligence

      - ARP – Address Resolution Protocol

      - DHCP - Dynamic Host Configuration Protocol

      - DNS - Domain Name Server

      - DDNS – Dynamic DNS

      - DORI - Detect, Observe, Recognize, Identify

      - fps - frames per second

      - HEVC – High Efficiency Video Coding

      - HTTPS – Secure Hypertext Transfer Protocol

      - ICMP - Internet Control Message Protocol

      - IP - Internet Protocol

      - IR – InfraRed

      - JPEG - Joint Photographic Experts Group

      - mDNS – Multicast DNS

      - MP - Megapixel

      - MJPEG - Motion JPEG

      - NTP - Network Time Protocol

      - PKI - Public Key Infrastructure

      - PoE - Power over Ethernet

      - RTCP – Real-Time Control Protocol

      - RTP - Real-Time Transport Protocol

      - RTSP - Real-Time Streaming Protocol

      - TCP - Transmission Control Protocol

      - TPM - Trusted Platform Module

      - TLS – Transport Layer Security

      - UDP - User Datagram Protocol

    - Reference Standards

      - Emission

        - EN 55032 (Class A),

        - FCC 47 CFR, part 15 (class A)

        - ICES-003 Issue 7

        - VCCI-CISPR 32

        - EN 50121-4

      - Immunity

        - EN 50121-4

        - EN 50130-4

      - Basic standards

        - EN 61000-4-2

        - EN 61000-4-3

        - EN 61000-4-4

        - EN 61000-4-5

        - EN 61000-4-6

        - EN 61000-4-8

      - Reliability

        - EN 50130-5 Class IV-A

        - EN 60068-2-1

        - EN 60068-2-2

        - EN 60068-2-6

        - EN 60068-2-42

        - EN 60068-2-75

      - Safety

        - EN IEC 62368-1

        - EN IEC 62471

        - IEC 62368-1

        - UL 62368-1

        - CAN/CSA-C22.2 No. 62368-1 ed. 3

      - Environment

        - RoHS EU, 2011/65/EU EN IEC 63000:2018

        - 1999/45/EC and 1907/2006 REACH

        - 2012/19/EU WEEE

        - 94/62/EC Packaging

      - ONVIF conformance

        - EN 50132-5-2

        - EN 62676-2

  - SUBMITTALS

    - Informational Submittals

      - Product Data

        - Manufacturer’s printed or electronic data sheets

        - Manufacturer’s installation and operation manuals

        - Warranty documentation

      - Shop Drawings

      - Cyber hardening guidance

    - Closeout Submittals

      - Final listing of devices and settings

      - System test results

      - Statement of compliance with Manufacturer Cyber Hardening Guidelines

  - QUALIFICATIONS

    - Installers shall be certified, trained and authorized by the Manufacturer to install, integrate, test, and commission the system.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver the camera in the manufacturer’s original, unopened, undamaged container with identification labels intact.

    - Store the camera in a temperature environment protected from mechanical and environmental conditions as designated by the manufacturer.

  - WARRANTY AND SUPPORT

    - Manufacturer shall provide a limited 5-year warranty for the product to be free of defects in material and workmanship.

END OF SECTION

- PRODUCTS

  - EQUIPMENT

    - Manufacturer: 	IQSIGHT LLC

130 Perinton Parkway

Fairport, New York, 14450

USA

Phone: +1 800-289-0096

Fax: +1 800-315-0470

Email: video.systems@iqsight.com

https://www.iqsight.com

IQSIGHT B.V.
Achtseweg Zuid 173
5651 GW Eindhoven
The Netherlands

Phone: + 31 40 2577 202

Fax: +31 40 2577 330

video.systems@iqsight.com

https://www.keenfinity-group.com

KEENFINITY PTE. LTD.

11 Bishan Street 21

Singapore 573943

Phone: +65 6571 2600

Fax: +65 6571 2698

video.systems@iqsight.com  
apr.sales@keenfinity-group.com

https://www.keenfinity-group.com

    - Product Model:	NDM-7712-AL

  - GENERAL DESCRIPTION

    - The camera shall be a 4x3 MP multi dome camera with integrated surround IR illumination, starlight, HDR X – Motion Optimized, H.264 and H.265 encoding, dynamic range of 120 dB, and built-in artificial intelligence providing full situational awareness and triggers for relevant alerts.

    - The fixed multi camera shall possess the following primary characteristics:

      - H.264, H.265, and MJPEG compression

      - Resolution up to 2048 x 1536 (4:3)

      - Built-in IR illumination: up to 30 m (98 ft)

      - Starlight and HDR X technology: up to 120 dB

      - Frame rate: up to 30 fps

      - Suite of deep learning-based video analytics and each sensor can run a different type of analytics

      - Four 3MP imagers at 30 fps in one camera on a single IP address that allows for full 360º coverage

      - DORI technology to facilitate distinguishing of persons or objects

      - The fixed multi camera shall incorporate multiple advanced data security elements, including a Cryptographic Coprocessor (Secure Element) supporting RSA 4096-bit, 512-bit ECC elliptic curves, and AES/CBC 256 bit encryption, a full Public Key Infrastructure (PKI) framework, recognized Certified Security Standards such as FIPS 140-3 Level 3, IEC 62443-4-2, and UL 2900-2-3, and update capability for future software security enhancements.

      - Available posting to cloud-based services

      - Pre-configured optimized scene modes

      - Remote camera management

      - Mobile device camera setup and configuration

      - IP66, UL Type 4X, and IK10 environmental ratings

      - PoE++ IEEE 802.3bt Type 3, Class 5

  - ADDITIONAL VIDEO/CAMERA SPECIFICATIONS

    - Imaging Device:

      - The fixed multi camera shall offer a 4x 1/2.8-inch CMOS image sensor.

      - The fixed multi camera shall offer a maximum effective number of pixels of 2048 x 1536 (3 MP) per sensor.

    - Lens:

      - The fixed multi camera shall offer an Automatic Varifocal (AVF) lens with fixed iris and a focal length of 3.2 to 8.1 mm.

      - The fixed multi camera shall offer a lens aperture of F/1.9 to F/3.2.

      - The fixed multi camera shall have a horizontal field of view of 104º to 37º.

      - The fixed multi camera shall have a vertical field of view of 73º to 28º.

      - The fixed multi camera shall offer motorized focus and fixed iris control with manual override.

    - Video Streaming:

      - The fixed multi camera shall provide direct network connection using H.265, H.264 and M-JPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

      - The fixed multi camera shall provide one M-JPEG and at least three H.264/H.265 independently configurable streams.

      - The fixed multi camera shall support the following video resolutions:

        - 3 MP (4:3), 2048 x 1536 to 0.3 MP (4:3), QVGA (4:3) 320 x 240.

      - The fixed multi camera shall have support for both 4:3 - wide screen and 3:4 - upright aspect ratios.

      - The fixed multi camera shall deliver 3 MP video, at rates up to 30 images per second.

      - The fixed multi camera shall offer a High Dynamic Range of 120 dB for clear images in extreme high-contrast environments.

    - Additional Video Functions:

      - The fixed multi camera shall support day/night modes with automatic adjustable switch points, allowing it to operate in both color and monochrome settings.

      - The fixed multi camera shall include backlight compensation.

      - The fixed multi camera shall offer video watermarking capabilities.

      - The fixed multi camera shall provide display stamping.

      - The fixed multi camera shall be capable of displaying its location information.

      - The fixed multi camera shall support a white balance range from 2,000 K to 10,000 K.

      - The fixed multi camera shall offer multiple white balance modes, including:

        - Standard

        - Hold mode

        - Sodium lamp

      - The fixed multi camera shall allow the definition of an area within the Field of View (FOV) as an exposure priority area, enhancing the visibility of objects in that specified area.

      - The fixed multi camera shall offer the ability to define up to 8 privacy masks per sensor.

      - The fixed multi camera shall offer multiple user defined privacy masks patterns, including:

        - Off

        - Auto

        - Black

        - White

        - Gray

        - Custom color

      - The fixed multi camera shall produce a monochrome image with a minimum scene illumination of 0.003 lux.

      - The fixed multi camera shall produce a color image with a minimum scene illumination of 0.035 lux.

      - The fixed multi camera shall offer IR illumination up to 30 m (98 ft).

      - The fixed multi camera shall allow for manual override to individually configure the IR intensity of each LED.

      - The fixed multi camera shall offer HDR (High Dynamic Range) X to enhance image quality in both bright and dark areas.

      - The fixed multi camera shall offer HDR X Motion optimized.

      - The fixed multi camera shall offer starlight technology to deliver superior image performance in low-light environments.

      - The fixed multi camera shall support Intelligent Defog to automatically adjust the contrast of the image in foggy scenes.

      - The fixed multi camera shall offer comprehensive video content analysis capabilities, including detection and classification of persons and vehicles.

      - The fixed multi camera shall offer a wide range of video analytics rule configuration, including:

        - Any object

        - Object in field

        - Line crossing

        - Enter / leave field

        - Loitering

        - Follow route

        - Idle object

        - Removed object

        - Counting

        - Occupancy

        - Condition change

        - Similarity search

        - Objects starting to move

        - Objects stopping

      - The fixed multi camera shall be configurable to execute the following actions upon alarm activation:

        - Turn its built-in output on or off

        - Turn another supported camera output on the same network on or off

        - Stream video to a compatible decoder

        - Send an e-mail with an image attachment

    - Local SD storage

      - The fixed multi camera shall have two microSD card slots that use standard off-the-shelf SD (Secure Digital) up to 2 TB, SDHC (Standard Digital High Capacity) or SDXC (Secure Digital eXtended Capacity).

      - The fixed multi camera shall support multiple recording modes, including manual, scheduled, pre-alarm and alarm recording.

      - The fixed multi camera shall support multiple storage configurations, including:

        - Mirror (redundant storage)

        - Failover (extended service interval)

        - Extend (maximum retention time)

        - Automatic Network Replenishment

      - The fixed multi camera shall offer enhanced system flexibility with dual recording (iSCSI and SD card) options.

      - The fixed multi camera shall support health monitoring on the microSD cards.

      - The fixed multi camera shall support uploading JPEG images with video analytics overlay to an FTP server.

    - Audio

      - The fixed multi camera shall provide switchable audio input. This includes one (1) line-in level (40 kOhm typical, 0.6 Vrms max).

      - The fixed multi camera shall provide one (1) audio line out (10 kOhm typical, 1.0 Vrms).

      - The fixed multi camera shall offer the G.711 8 kHz, L16 16 kHz, AAC-LC 80 kbps 16 kHz and 48 kbps 16 kHz compression rates.

      - The fixed multi camera shall provide full duplex and half duplex streaming.

      - The fixed multi camera shall be capable of disabling audio input permanently with a license code.

    - ONVIF

      - The fixed multi camera shall conform to the ONVIF Profile S, G, T and M.

    - Video Analytics

      - The fixed multi camera shall offer embedded deep learning-based detection and video analytics (IVA Pro) that eliminate dedicated PCs and associated software maintenance.

      - The fixed multi camera shall offer embedded IVA Pro Buildings, IVA Pro Perimeter and IVA Pro Privacy (available with a future FW release) for reliable deep learning-based detection.

      - The fixed multi camera shall support other license options, including:

        - IVA Pro Traffic

        - IVA Pro Appearance

        - IVA Pro PPE

        - IVA Pro Gunshot Detection (Audio - available with a future FW release)

      - The fixed multi camera shall provide Camera Trainer to allow the user to train the system for custom object detection and classification.

      - The fixed multi camera shall support one IVA Pro analytics package per imager. A single licensed IVA Pro package may be deployed on all imagers simultaneously or different packages may be assigned to each imager as required. Only one license per camera is required to enable operation on all imagers.

      - The fixed multi camera shall be capable of running 16 different video analytics rules simultaneously.

      - The fixed multi camera shall support automatic switching of video analytics types according to a predefined schedule.

      - The fixed multi camera shall be capable of generating metadata, including object speed, geolocation, height, width, and classification to be recorded with the video.

      - The fixed multi camera shall be capable of detecting and classifying up to 64 objects.

      - The fixed multi camera shall support machine learning to enable users to classify customized objects.

  - NETWORK

    - Connectivity:

      - The fixed multi camera shall offer versatile network connectivity options, such as 10/100/1000BASE-T Ethernet interfaces.

      - USB-C port for local commissioning via wireless USB dongle.

    - Protocols supported:

      - The fixed multi camera shall support the following protocols:

        - Transmission: Internet Protocol (IP) v4 and v6, Transmission Control Protocol (TCP), and User Datagram Protocol (UDP).

        - Configuration: Dynamic Host Configuration Protocol (DHCP) for automatic IP assignment, fixed IP addressing for static deployments, and Automatic Private IP Addressing (APIPA) for link-local fallback.

        - Web Services: Internet Control Message Protocol (ICMP) and ICMPv6 for diagnostics and error reporting; Hypertext Transfer Protocol (HTTP), Secure HTTP (HTTPS), and HTTP Strict Transport Security (HSTS) for secure web-based management.

        - Network Services: Address Resolution Protocol (ARP) for IP-to-MAC mapping; Domain Name System (DNS/DNSv6) and Dynamic DNS (DDNS) with DynDNS.org support for flexible hostname resolution; Network Time Protocol (NTP/SNTP) for accurate time synchronization; File Transfer Protocol (FTP) for secure file exchange; Simple Network Management Protocol (SNMP v1 and v3, MIB-II) for monitoring and management; Syslog for centralized logging and event collection.

        - Media Streaming: Real-Time Transport Protocol (RTP) and Real-Time Control Protocol (RTCP) for audio/video streaming; Real-Time Streaming Protocol (RTSP) and Secure RTSP (RTSPS) for session control; Secure RTP (SRTP) for encrypted media streams; Internet Group Management Protocol (IGMP v2/v3) for multicast optimization; Differentiated Services (DiffServ) for Quality of Service (QoS).

        - Advanced & IoT: Link Layer Discovery Protocol (LLDP) for device identification and topology mapping; Simple Object Access Protocol (SOAP) for integration with web services; Message Queuing Telemetry Transport (MQTT) and Secure MQTT (MQTTS) for IoT communication; Simple Mail Transfer Protocol (SMTP) for email notifications; Internet Small Computer Systems Interface (iSCSI) for storage-related communication.

    - Data Security

- The fixed multi camera shall incorporate multiple advanced data security elements, including a Cryptographic Coprocessor (Secure Element) supporting RSA 4096-bit, AES/CBC 256-bit, and 512-bit ECC elliptic curves, ensuring robust cryptographic operations and secure key storage.

- The fixed multi camera shall implement a comprehensive Public Key Infrastructure (PKI) framework, including:

  - X.509 certificates for secure identity management.

  - Support for SCEP (Simple Certificate Enrollment Protocol).

  - Device identity certificate anchored to a Root CA.

  - Embedded firewall for enhanced network protection.

- The fixed multi camera shall support end-to-end encryption when integrated with compatible VMS platforms, ensuring confidentiality of video streams and control data.

- The fixed multi camera shall provide strong encryption protocols, including TLS 1.3 and TLS 1.2 for secure communication, and AES 256-bit and AES 128-bit for data protection.

- The fixed multi camera shall support multiple network authentication methods, including IEEE 802.1X, EAP/TLS, CHAP, Digest Authentication, and configurable session timeout for secure access control.

- For local storage encryption, the fixed multi camera shall utilize AES-XTS to protect recorded data against unauthorized access.

- The fixed multi camera shall implement a Signed Video Framework, supporting Checksum verification, MD5, SHA-1, and SHA-256 to ensure video integrity and authenticity.

- The fixed multi camera shall provide advanced firmware protection mechanisms, including Signed Firmware, Secure Boot, Software Sealing, SBOM (Software Bill of Materials), and Cloud Firmware Check to prevent tampering and ensure trusted updates.

- The fixed multi camera shall comply with globally recognized Certified Security Standards, including:

- Common Criteria EAL6+ (Secure Element 3.0).

- FIPS 140-3 Level 3 (Secure Element 3.0).

- IEC 62443-4-1, IEC 62443-4-2, and UL 2900-2-3 for industrial cybersecurity and product assurance.

  - ELECTRICAL

    - Power Input:

      - The fixed multi camera shall support the following redundant power options:

        - 24 VAC

        - 24 VDC

        - PoE++ IEEE 802.3bt Type 3, Class 5

        - PoE+ 802.3at Type 2, Class 4 (operating temperature -20 ºC to +55 ºC / -4 ºF to +131 ºF)

    - Power Consumption (maximum)

      - The fixed multi camera shall support the following maximum power consumption options:

        - VAC: 20.4 W (Without IR, Heater), 41.7 W (With IR, Heater)

        - VDC: 20.4 W (Without IR, Heater), 39.1 W (With IR, Heater)

        - PoE: 22.2 W (Without IR, Heater), 40 W (With IR, Heater)

  - MECHANICAL AND ENVIRONMENTAL

    - Material:

      - The fixed multi camera shall offer an anodized cast aluminum, rugged design and polycarbonate housing.

    - Finish:

      - The fixed multi camera shall offer a white finish.

    - Impact Resistance:

      - The fixed multi camera shall offer IK10 impact resistance housing and bubble.

    - Dimensions (Ø x H):

      - The fixed multi camera shall have 260 mm x 133 mm (10.24 in. x 5.24 in.).

    - Temperature:

      - The fixed multi camera shall support an operating temperature range of -50 ºC – 55 ºC (-58 ºF – 131 º F) for continuous operation (PoE++, with heater).

      - The fixed multi camera shall support a storage temperature range of -40 ºC to 70 ºC (-40 ºF to 158 ºF).

    - Relative Humidity (non-condensing):

      - The fixed multi camera shall support an operating relative humidity of 5% to 93%.

      - The fixed multi camera shall support a storage relative humidity of up to 98%.

    - Ingress Protection

      - The fixed multi camera shall offer IP66 environmental protection.

    - Mounting:

      - The fixed multi camera shall offer accessories to enable the mounting of the box camera in the following circumstances:

        - Pendant wall mount

        - Wall mount

        - Pendant pipe mount

        - Pole mount

        - Pendant parapet mount

        - Corner mount

  - ACCESSORIES

    - Hardware accessories:

      - NDA-7052-PIPW		Pendant Interface Plate

      - NDA-U-WMT			Pendant wall mount

      - NDA-U-WMP			Wall mount plate

      - NDA-U-PMT			Pendant pipe mount, 12" (31cm)

      - NDA-U-PMTE			Pendant pipe extension, 20" (50cm)

      - NDA-U-PMTS			Pendant pipe mount, 4" (11 cm)

      - NDA-U-PSMB			Pendant wall/ceiling mount SMB

      - NDA-U-PMAS			Pole mount adapter small

      - NDA-U-PMAL			Pole mount adapter large

      - NDA-U-RMT			Pendant parapet mount

      - NDA-U-CMT			Corner mount adapter

      - NDA-U-PMTG			Pendant pipe mount, gang box

      - NDA-U-WMTG			Pendant wall mount, gang box

      - NDA-U-PA0			Surveillance cabinet 24VAC

      - NDA-U-PA1			Surveillance cabinet 120VAC

      - NDA-U-PA2			Surveillance cabinet 230VAC

      - NCA-WLAN-EU			Wireless installation dongle EU

      - NCA-WLAN-NA			Wireless installation dongle NA

      - NPD-6001C			Midspan, bt, 60W, indoor

      - NPD-6001C-E			Midspan, bt, 60W, IP67

      - NPD-6001-I			Midspan, bt, 60W, indoor, industrial

      - NPD-9001-E			Midspan, bt, 90W, IP67

      - NPD-9001-EBT			Midspan bt 90W IP67 TAA

      - VG4-SFPSCKT			Ethernet to SFP interface kit

      - SFP-2				Fiber module, multimode, 1310nm, 2LC

      - SFP-3				Fiber module, single-mode, 1310nm, 2LC

      - SFP-25				Fiber module, 1310/1550nm, 1SC

      - SFP-26				Fiber module, 1550/1310nm, 1SC

      - MSD- V256G			Surveillance microSD card 256GB

      - MSD-V512G 			Surveillance microSD card 512GB

      - MSD-V1T00			Surveillance microSD card 1TB

      - MSD-V1T50			Surveillance microSD card 1.5TB

    - Software options

      - MVC-IVA-TRA 			IVA Pro Traffic

      - MVC-IVA-APC 			IVA Pro Appearance

      - MVC-IVA-PPE 			IVA Pro PPE

      - MVC-IAA-GUN			Gunshot Detector License, perpetual

END OF SECTION

- EXECUTION

  - INSTALLERS

    - Contractor personnel shall comply with all applicable state and local licensing requirements.

  - PREPARATION

    - The network design and configuration shall be verified for compatibility and performance with the camera(s).

    - Network configuration shall be tested and qualified by the Contractor prior to camera installation.

    - Before permanent installation of the system, the Contractor shall test the system in conditions simulating the final installed environment.

  - INSTALLATION

    - The contractor shall follow all Manufacturer-published guidance on proper installation and configuration of the installed cameras.

    - The Contractor shall test the system in conditions simulating the final installed environment

    - Reports:

      - System test results

      - System network addressing and device settings

  - STORAGE

    - Products shall be stored in an environment where temperature and humidity are in the range specified by the Manufacturer.

END OF SECTION

202610151033